## Points list
Controller | Point name | Descriptor | Point type | Field device | Signal / units | Location | Alarm / trend | Notes
AHU-1 controller | AHU1-SF-SS | Supply fan start/stop | BO | Supply fan starter relay | Dry contact | AHU-1, Mech Room 101
AHU-1 controller | AHU1-SF-STS | Supply fan status | BI | Current switch | Dry contact | AHU-1, Mech Room 101 | Alarm on failure | Proof of operation
AHU-1 controller | AHU1-SAT | Supply air temp | AI | Duct temperature sensor | 10k thermistor, °F | AHU-1 supply duct | Alarm high/low, trend
AHU-1 controller | AHU1-RAT | Return air temp | AI | Duct temperature sensor | 10k thermistor, °F | AHU-1 return duct | Trend
AHU-1 controller | AHU1-MAT | Mixed air temp | AI | Averaging temperature sensor | 10k thermistor, °F | AHU-1 mixing box | Trend
AHU-1 controller | AHU1-OAT | Outside air temp | AI | Outdoor temperature sensor | 10k thermistor, °F | North wall, shaded | Trend | May be shared from another controller
AHU-1 controller | AHU1-OAD | Outside/return air dampers | AO | Damper actuator | 0-10 V | AHU-1 mixing box
AHU-1 controller | AHU1-CHW-VLV | Chilled water valve | AO | 2-way valve actuator | 0-10 V | AHU-1 cooling coil
AHU-1 controller | AHU1-HW-VLV | Hot water valve | AO | 2-way valve actuator | 0-10 V | AHU-1 heating coil
AHU-1 controller | AHU1-FLT-DP | Filter differential pressure | BI | Differential pressure switch | Dry contact | AHU-1 filter bank | Alarm | Dirty filter
AHU-1 controller | AHU1-FRZ | Low temperature detection | BI | Freeze stat | Dry contact | AHU-1 leaving heating coil | Alarm | Hardwired fan shutdown
AHU-1 controller | AHU1-SAT-SP | Supply air temp setpoint | AV | Software point | °F |  |  | Adjustable
AHU-1 controller | AHU1-OCC | Occupancy mode | BV | Software point | Occupied / Unoccupied |  | Trend | From schedule

## Point types
Type | Meaning | Typical use
AI | Analog input | Temperature, pressure, humidity sensors
AO | Analog output | Valve or damper actuator, VFD speed command
BI | Binary input | Fan status, filter alarm, freeze stat
BO | Binary output | Fan or pump start/stop
AV / BV / MSV | Analog, binary or multi-state value | Setpoints, modes, schedules

## About
BAS points list template, by Structio (structioarchi.com/en).
Example: a constant-volume air handler with mixed air dampers, chilled water and hot water coils. Replace it with your own job.
Guide: https://structioarchi.com/en/guides/bas-points-list
Structio builds the points list and the network riser from one project description: https://structioarchi.com/en